| LHC- - - 1999-09-22 |
| --- |
| Stepping motors control |
| Prepared by: Jacky Brahy AB/CO Jacky.Brahy @cern.ch | Checked by: | Approval Leader : |
| Approval list: |
| History of Changes |
| Rev. No. | Date | Pages | Description of Changes |
| Release | 24-July-2008 |  | First version |

1.	INTRODUCTION	4

2.	ENVIRONMENT	4

3.	CONTROLER DESCRIPTION	4

3.1	Product Overview	4

3.2	Parameters and Settings	4

3.3	Search for Reference	5

3.4	Moving	6

4.	TYPES OF INSTALLATIONS	7

4.1	Installation with Encoder	7

4.2	Installation without Encoder	7

5.	HARDWARE CONFIGURATION	9

6.	FUNCTION DESCRIPTION	10

6.1	Interfacing the Function	10

6.1.1	Input Parameters	10

6.1.1	Output Parameters	12

6.2	Control Modes	13

6.2.1	Remote Mode	13

6.2.2	Manual Mode	13

6.2.3	Local Mode	14

6.2.4	Switch of Modes	14

6.2.4.1	Organization of Modes	14

6.2.4.2	Switch from any mode to manual or local	15

6.2.4.3	Switch from manual or local to remote	15

6.3	Initialization of the Function	16

6.3.1	Startup	16

6.3.2	Configuration Parameters	16

6.4	Function Diagram	17

6.5	Running Sequences	19

6.5.1	Search Reference	19

6.5.2	Move to Destination	20

6.5.3	Stop	21

7.	PARTICULAR BEHAVIOURS	22

7.1	Reaching limit Switch during Movement	22

8.	SYSTEM COMMISSIONING	23

8.1	Selection of Movement Direction	23

8.2	Determine the Reference Position	24

8.2.1	Without Encoder	24

8.2.2	With Encoder	24

8.3	Determine the Software Limits	24

9.	POWER DRIVER	25

9.1	New and Old Systems	25

9.2	Type of Power Driver	25

9.3	Characteristics  OF ZSX MICRO 256	26

9.4	Characteristics of ZSO MINI	27

9.5	Standard  Power Crate	31

10.	ANNEXES	34

10.1.1	ANNEXE 1: Stepmotor Class	34

10.1.2	ANNEXE 2: Programming Example	36

10.1.3	ANNEXE 2: Local Panel Example	38

# INTRODUCTION

Many systems have to be controlled by stepping motors, in order to minimize the development and maintenance a set of generic functions has been created.

# ENVIRONMENT

Software requirement.

STEP7 and SCL for the libraries

WinCC flexible for touch panel

Hardware requirement

The stepping controller must be the “1STEP 5V/204kHz” ES200S module.

# CONTROLER DESCRIPTION

## Product Overview

The 1STEP 5V/204kHz generates pulses and a directional signal for the power

units of stepping motors. The number of pulses emitted determines the distance

traversed. The pulse frequency determines the velocity. The way the

1STEP 5V/204kHz works depends on its parameters and settings.

The 1STEP 5V/204kHz has the following features:

• Digital input as reference cam

• Digital input as external STOP or external pulse enable

• Interface to commonly available stepping motor power units with differential

signals for pulses and direction to RS 422

• Maximum output frequency 204 kHz

• Distance up to 1 048 575 pulses

## Parameters and Settings

The basic parameters are assigned in the hardware manager of Step7.

- Base Frequency: Fb

- Multiplier: n

These 2 parameters determine the Start-Stop frequency Fss

- Time interval: i

This parameter determine the acceleration/deceleration

Two other parameters are transmitted to controller trough the command interface

- Multiplier: G

- Reduction factor: R

The resulting controller parameters are the followings:

- Start-stop frequency: Fss=Fb*n*R

The possible range is 0.4 Hz to 204 kHz

- Acceleration: a=Fb*R/(i*0.128 mS) in Hz/ms

The possible range is 0.012 Hz/ms to 6250 Hz/ms

- Output frequency: Fa=Fss*G

The possible range is 0.4 Hz to 204 kHz

## Search for Reference

After a start or restart of the controller, the reference point is not defined, a search for reference sequence as to be executed.

The execution of this sequence depends of the initial position. The 4 possible scenarios are shown in the following table.

The motor has always to start in the DIR_P (move to the LIMIT_P end switch) direction. At the end of the sequence the actual position is the reference position; this a parameter determine by the user of the system.

## Moving

This is the normal mode. The distance to move and the direction are given to the controller which

- start at the start-stop frequency

- accelerate up to the output frequency

- move to destination

- decelerate down to start-stop frequency

- stop

# TYPES OF INSTALLATIONS

Two types of installation are supported:

- The installation with encoder

- The installations without encoder

A specific function corresponds to each case.

## Installation with Encoder

In this version, two types of encoder are supported, Linac or Moore Reed. The selection is made with the input parameters of the corresponding function. The treatment of the encoders acquisition and decoding is made in separate functions.

In this case the installation doesn’t need to have a reference switch but the search to reference sequence must nevertheless be executed; the “1STEP 5V/204kHz” controller can’t work without this initialisation. The reference switch is simulated with a digital output.

## Installation without Encoder

This is the typical application of the “1STEP 5V/204kHz” controller the sequence describe in 3.3 is executed at the beginning.

Reference switch available:

For standard installation, the reference switch (NO) is connected to the corresponding input of the 1STEP controller.

No reference switch available:

Some old installations don’t have a reference switch and are not easy to modify. To solve this problem the CW end switch is used as a reference switch.

First case:

The CW end switch is read through a digital input, inverted and send to REF input of the 1STEP controller through a digital output.
In this case, a reaction delay equal to cycle time of the PLC is introduced. For precise positioning, the 2nd solution is recommended.

No particular accuracy requested

Second case:

The 24V DO module must be must be replaced by a DO relay.

The CW end switch is read through a digital input, inverted and send to REF input of the 1STEP controller through a digital output. This part is used to simulate the ref switch crossing.
For the end of movement sequence, the CW end switch is sent directly to the REF input of the 1 STEP controller through the contact of the relay output. This is to improve reaction time and then the accuracy of positioning.

High accuracy requested

# HARDWARE CONFIGURATION

Inside a station, the input addresses must be contiguous and the module addresses must be incremented by 1 byte.

1 station with encoder

2 stations with encoder

2 stations without encoder

# FUNCTION DESCRIPTION

The function manage the commands to the controller

## Interfacing the Function

### Input Parameters

The input parameters are divided in 6 categories.

- The hardware parameters set by the application program: 
The addresses of physical modules. Motor_Controler_Addr, DO_Addr, DI_Addr     
The type encoder used: Encoder_Type

- The physical parameters set by the application program:
One of the parameters of the basic speed: Reduction
The ratio steps motor/steps encoder: Factor_Encoder
The ratio speed/basic speed: G_multiplier

- The configuration parameters set by the remote station: 
These parameters can only be sent by the remote station through the IEPLC communication DB.
 The reference position (for applications without encoder): Ref_Position
The maximum software limit: In_Max_limit
The minimum software limit: In_Min_limit
The physical scale: In_Scal
The physical offset: In_Offset
The configuration settings: IePlcConfig

- The remote control command send by the remote station:
These parameters are sent through the IEPLC communication DB.
The remote control request: one bit of AutoReg
The stepping controller mode: Auto_Mode_Command
The new position: Auto_Set_Position

- The manual mode commands: send by the manual controller (Optionnal)
The manual control request: Manreg01 (take or release manual mode)
The stepping controller mode: Manu_Mode_Command
The new position: Manu_Set_Position

- The local mode commands: send by the local panel (Optionnal)
The local control request: Locreg01 (take or release local mode)
The stepping controller mode: Local_Mode_Command
The new position: Local_Set_Position

| Parameter name | I/O | Type | Description |
| --- | --- | --- | --- |
| Motor_Controler_Addr | IN | INT | Hardware address of the motor controler |
| DO_Addr | IN | INT | Beginning of digital output addresses |
| DI_Addr | IN | INT | Beginning of digital input addresses |
| ColdStart | IN | BOOL | Cold start request |
| Reduction | IN | BOOL | Reduction factor (speed/10) if TRUE |
| Encoder_Type | IN | BYTE | 0=Encoder Linac; 1=Encoder Moor reed: for application with encoder only |
| G_multiplier | IN | INT | Ratio between start/stop and move speed |
| Factor_Encoder | IN | INT | Number of motor step per encoder step: for application with encoder only |
| AutoReg | IN | WORD | Remote Commands |
|  |  |  | Bit 0: | New position request (not used) |
|  |  |  | Bit 1: | New mode request (not used) |
|  |  |  | Bits 2..6: | Spare |
|  |  |  | Bit 7: | Remote mode request |
|  |  |  | Bits 8..15: | Spare |
| Manreg01 | IN | STRUCT | Manual Commands |
|  | MAuMoR | BOOL | Remote control mode request |
|  | MMMoR | BOOL | Manual control mode request |
|  |  | END_STRUCT |  |
| Locreg01 | IN | STRUCT | Local Commands |
|  | LAuMoR | BOOL | Remote control mode request |
|  | LLoMoR | BOOL | Local control mode request |
|  |  | END_STRUCT |  |
| Auto_Set_Position | IN | REAL | Remote position request |
| Manu_Set_Position | IN | REAL | Manual position request |
| Local_Set_Position | IN | REAL | Local position request |
| Auto_Mode_Command | IN | WORD | Remote mode command | 0 = Normal 1 = Ref. position 2 = Stop |
| Manu_Mode_Command | IN | WORD | Manual mode command |  |
| Local_Mode_Command | IN | WORD | Local mode command |  |
| Ref_Position | IN | REAL | Physical position after the search reference position sequence |
| In_Min_limit | IN | REAL | Software minimum position to go |
| In_Max_limit | IN | REAL | Software maximum position to go |
| In_Scal | IN | REAL | Parameters for physical to absolute (in motor steps) position transformation. AbsPosition = (PhysPosition / Scal) + Offset) |
| In_Offset | IN | REAL |  |
| IePlcConfig | IN | WORD | Remote Commands |
|  |  |  | Bit 0: | Set configuration |
|  |  |  | Bit 1: | Used speed (future use) |
|  |  |  | Bit 2: | No reference switch (see ??????) |
|  |  |  | Bit 3..7: | Spare |
|  |  |  | Bits 8..15: | Spare |

### Output Parameters

Detailed description

| Parameter name | I/O | Type | Description |
| --- | --- | --- | --- |
| Status1 | OUT | WORD | Bit 0: | Object is enable |
|  |  |  | Bit 1: | Object is disable |
|  |  |  | Bit 2: | Object is in Remote mode |
|  |  |  | Bit 3: | Object is in Manual mode |
|  |  |  | Bit 4: | Object is in forced mode (not used) |
|  |  |  | Bit 5: | Object is in Local control mode |
|  |  |  | Bits 6..7: | Spare |
|  |  |  | Bits 14..15: | Spare |
| Status2 | OUT | WORD | Bit 0: | Object is in Normal mode |
|  |  |  | Bit 1: | Object is in Search reference |
|  |  |  | Bit 2: | Object is in Stop |
|  |  |  | Bit 3: | The configuration parameters have been transmitted |
|  |  |  | Bit 4: | Object is executing a movement |
|  |  |  | Bit 5: | Motor with encoder |
|  |  |  | Bit 6: | Encoder is Linac |
|  |  |  | Bit 7: | Encoder is Moor Reed |
|  |  |  | Bit 8: | Error job from step controller |
|  |  |  | Bit 9: | Illegal move: a move request is sent when the control is searching the reference or is not synchronized |
|  |  |  | Bit 10: | Encoder not connected |
|  |  |  | Bit 11: | Step controller not synchronized |
|  |  |  | Bit 12: | Time for search reference or move exceeded |
|  |  |  | Bit 13: | Spare |
|  |  |  | Bit 14: | CW limit reached |
|  |  |  | Bit 15: | CCW limit reached |
| Mode_Command | OUT | WORD | Actual object mode (Normal, Search ref. or Stop) |
| Obj_Set_Position | OUT | REAL | Physical request position of the object |
| Obj_Actual_Position | OUT | REAL | Physical actual position of the object |
| Abs_Actual_Position | OUT | DINT | Actual position in number of steps |
| Max_Limit | OUT | REAL | Actual maximum software limit |
| Min_Limit | OUT | REAL | Actual minimum software limit |
| Used_Scal | OUT | REAL | Actual scale | Parameters for physical to absolute (in motor steps) position transformation. |
| Used_Offset | OUT | REAL | Actual offset |  |

## Control Modes

The function supports three mode of command.

- Remote mode

In this mode, the input and output parameters of the function are coming or sent to an external data block. This mode is typically used when a remote control through IEPLC

- Manual mode

This mode has been designed to take the control from a PVSS application which could run on a laptop placed locally and used by the specialist of the system.

- Local mode

This model permits the control through a touch panel installed permanently and used by the specialist of the system.

### Remote Mode

The motor is controlled from a remote station using the STEPMOTOR FESA class and the IEPLC communication. The IEPLC configuration tool creates a source file which will be compiled in order to create the appropriate IEPLC Data Block. The structure of this DB corresponds to the STEPMOTOR class structure (See ANNEXE 1). The remote command and acquisition will be written to or read from this DB.

| IEPLC DB |  | IN/OUT parameters of Function |
| --- | --- | --- |
| Command (CMD) |
| CMD.commandMode |  | Auto_Mode_Command |
| CMD.requestedPosition |  | Auto_Set_Position |
| CMD.order |  | AutoReg |
| Configuration (CFG) |
| CFG.refPosition |  | Ref_Position |
| CFG.minPosition |  | In_Min_limit |
| CFG.maxPosition |  | In_Max_limit |
| CFG.scalingfactor |  | In_Scal |
| CFG.offset |  | In_Offset |
| CFG.config |  | IePlcConfig |
| Acquisition (AQN) |
| AQN.actualPosition |  | Obj_Actual_Position |
| AQN.targetPosition |  | Obj_Set_Position |
| AQN.status1 |  | Status1 |
| AQN.status2 |  | Status2 |

As long as the configuration parameters have not been sent, it’s not possible to send any command to control function. The bit 3 of Status2 indicates that this action has been performed.

### Manual Mode

The specialist can take the control manually using a Laptop running PVSS and communication with the PLC through Ethernet. The inputs and outputs used are the followings.

| Manreg01. MAuMoR |  | Release control (back in remote) from the manual station |
| --- | --- | --- |
| Manreg01. MMMoR |  | Take to control from the manual station |
| Manu_Set_Position |  | New position request from the manual station |
| Manu_Mode_Command |  | New mode command from the manual station |

### Local Mode

A touch panel can be installed locally (on the PROFIBUS fieldbus) to be used by the specialist for a visual control of the system.

The inputs and outputs used are the followings.

| Locreg01. LAuMoR |  | Release the control (back in remote) from the local station |
| --- | --- | --- |
| Locreg01. LLMoR |  | Take to control from the local station |
| Local_Set_Position |  | New position request from the manual station |
| Local_Mode_Command |  | New mode command from the manual station |

### Switch of Modes

This chapter describes the behaviour of the function when a change from one mode to another is requested.

#### Organization of Modes

The SetPosition and Command really used in the object can be taken from one of the three sources depending of the selected control mode (Remote, Manual, Local).

#### Switch from any mode to manual or local

When the function switches from “Remote” to “Manual” or “Local”, it takes care to avoid any reaction to the system. To achieve this goal, when a control request to Manual or Local is received, the function transfer object the Command and SetPosition to the corresponding Manual or Local parameters.

#### Switch from manual or local to remote

In this case, the object returns to the remote mode using the parameters in use when this mode had been leaved. It’s the responsibility of the operator to modify its parameters if he wants to continue with the last local or manual mode. To do this, he is informed of the status of the object by reading the acquisition values.

## Initialization of the Function

### Startup

The function must be initialized when the PLC Start. This is fulfilled by calling the function with the “ColdStart” input variable with a “TRUE” value. The function is then cyclically called with “ColdStart” at “FALSE”.

NB: After the download of an instance DB, the PLC must be restarted to fulfil this initialization.

### Configuration Parameters

The following configuration parameters

CFG.refPosition

CFG.minPosition

CFG.maxPosition

CFG.scalingfactor

CFG.offset

CFG.config

are defined in the STEPMOTOR class.

The corresponding input parameters of the function are shown in 6.2.1 and they are explained in 6.1.1.

The function can’t execute any action once it has not received the configuration parameters.

The configuration parameters are sent to the function when the “Remote” mode is selected, they are written in the IEPLC DB by the remote station. The paramaters are taken into account when the bit “Set Configuration” of CFG.Config is TRUE.

It’s possible to check wether the configuration has been done by reading the bit 3 of Status2 output parameter.

After the configuration has been done, a “Search Reference” command must be sent. Note that this command is initiated on a transition either from “Stop” or “Move”  to  “Search Reference”.

## Function Diagram

The diagram describes how the function executes its tasks.  The colours show the differences between systems with or without encoder.

- For system with encoders the reference point is the reading value of the encoder after the search reference action is finished.

- For systems without encoder the reference point is given in the configuration parameters.

The systems without encoder can have a reference switch or not. If there is no reference switch, the CW limit can be used as reference switch.

## Running Sequences

### Search Reference

The search to reference sequence is needed by the 1STEP controller before executing any operation. The aim is to determine the absolute position.

After the execution of the sequence, the absolute position is set to:

- The reference position given as a CFG parameter from the class for applications without encoder.

- Encoder position for applications with encoder.

| Without encoder | With encoder |
| --- | --- |

### Move to Destination

A number of steps of displacement and the direction of the displacement are sent to the controller.

| Without encoder | With encoder |
| --- | --- |

### Stop

Send a stop request to the 1STEP controller.

This command can be sent when the motor is stopped or executing a movement. In any case, the absolute position is not loosed after a STOP.

| Without encoder | With encoder |
| --- | --- |

# PARTICULAR BEHAVIOURS

## Reaching limit Switch during Movement

This situation should never appear when the commissioning of the installation has been correctly done, indeed, the software limits are inside the limit switches range. Nevertheless, if for any reason this situation appear,

- the movement will stop

- the time out indicator will appear (after 2 minutes)

After reaching the limit switch, the movement stopped normally without loosing the trace of the real position except if a mechanical obstacle is encountered.

The reason of problem should be detected and corrected before executing any action.

In order to recover a normal operation, it is strongly recommended to execute a SEARCH REFERENCE command as the absolute position is not guarantee (except for installations with encoder). If the absolute position seems to be correct and a SEARCH REFERENCE not welcome, the operation can continued by sending a STOP command followed by a MOVE command in the opposite direction.

# SYSTEM COMMISSIONING

## Selection of Movement Direction

The Step Controller parameters must match to the application.

- When the controller request a move to LIMIT_P, the motor has to move to CW limit, the encoder (if we have one) value must increase.

- When the controller request a move to LIMIT_M, the motor has to move to CCW limit, the encoder (if we have one) value must decrease.

How To fulfil the previous requirement:

The Step Controller provides RS422 driver for pulse and direction outputs, in our case, a single output is used in TTL mode. The interest is that we can choose the rotation direction of the motor by selecting the normal or complementary DIR output.

## Determine the Reference Position

### Without Encoder

After execution of the search reference sequence, the mechanical position of the controlled system must measured and introduce in the FESA equipment CFG parameters. The next time a search reference sequence is executed, the absolute position will be set to this value.

### With Encoder

The reference position parameter in the FESA equipment CFG parameter in empty. After execution of the search reference sequence, the value of the encoder will be set as the new absolute position.

## Determine the Software Limits

The software limits will be determined by the responsible of installation in collaboration with the PLC specialist. The software range must be inside the range given by the end switches.

These values will be introduce in the FESA equipment CFG parameters.

# POWER DRIVER

## New and Old Systems

The stepping motor control system is used for new installations or to rejuvenate old one.

In the old installations, two type of power crate are used.

For bipolar control, the Phytron power crate with 4 BD300 power drivers is used. The connection is made using a 12 pins burndy plug.

For unipolar control, a CERN made power driver is used.

A new power has been designed to replace both types of installations.

The connection is made using a 8 pins burndy plug.

In the new or rejuvenate, only bipolar control will be used, the unipolar old systems will be adapted as follow.

## Type of Power Driver

Two models of compatible Phytron power driver can be used:

- ZSX MICRO 256

- ZSO MINI

Actually the ZSX MICRO 256 is preferred due to the possibility of separately setting the drive and stop current. In the ZSO MINI, the stop current is automatically set to the half of the drive current.

The step motors are part of old installations and their characteristics are not known, it’s then difficult to adjust precisely the drive and stop current. An excessive warm-up can result of a to high stop current. The stop current is then set to zero in the ZSX MICRO 256 power driver.

## Characteristics  OF ZSX MICRO 256

## Characteristics of ZSO MINI

## Standard  Power Crate

# ANNEXES

### ANNEXE 1: Stepmotor Class

Command (CMD): (read/write)

“COMMAND”	WORD

0: Normal	(Mode: Normal)

1: Reference	(Mode: Reference)

2: Stop	(Request to stop move)

“POSITION”	REAL

Target position

“ORDER” 	WORD

bit 0: New position request	(for future use)

bit 1: New mode request	(for future use)

bit 2: spare

bit 3: spare

bit 3: spare

bit 4: spare

bit 5: spare

bit 6: spare

bit 7: Remote Mode Request

bit 8 to 15 : spare

Acquisition (AQN): (read-only)

“POS”		REAL		Current position

“SETPOS”	REAL		Current target position

“STATUS1”	WORD		Motor status part 1

bit 0: Object ON	(Object enable)

bit 1: Object OFF	(Object enable)

bit 2: object is in remote control mode

bit 3: object is in manual control mode

bit 4: spare

bit 5: object is in local control mode

bit 6: spare

bit 7: spare

bit 8 to 15:  spare

“STATUS2”	WORD 		Motor status part 2

bit 0: Move Position

bit 1: Search Reference

bit 2: Stop Move

bit 3: Configuration Done

bit 4: Busy

bit 5: With Encoder

bit 6: Linac Encoder

bit 7: Moore Reed Encoder

bit 8: Error Job

bit 9: Illegal Move

bit 10: Encoder Not Connected

bit 11: Not Synchronized

bit 12: Time OUT

bit 13: spare

bit 14: ILIMIT-CW

bit 15: ILIMIT-CCW

Configuration (CFG): (read/write)

“REF.  POSITION”	REAL		Position given by reference switch

“MIN”			REAL		Minimum target position

“MAX”			REAL		Maximum target position

“SCAL”			REAL		Scaling factor

“OFFS”			REAL		Offset value

“CONFIG”		WORD

bit 0: Set Configuration

bit 1: Use Speed  (Future implementation)

bit 2: Without Reference Switch

bit 3: spare

bit 4: spare

bit 5: spare

bit 6: spare

bit 7: spare

bits 8 to 15: spare

### ANNEXE 2: Programming Example

ORGANIZATION_BLOCK OB100

(***************************************************************************)

(*****               Clod Start Organisation Block                     *****)

(*****                                                                 *****)

VAR_TEMP

// Reserved

Info: ARRAY[0..19] OF BYTE;

// Temporary Variables

END_VAR

// Motor 1 Part

FB_Step_Without_Enc.DB_Motor_1_WithoutEnc(

Motor_Controler_Addr := 272 // IN: INT

,DO_Addr := 0 // IN: INT

,DI_Addr := 0 // IN: INT

,ColdStart :=  TRUE// IN: BOOL

,G_multiplier := 20 // IN: INT

);

// Motor 4 Part

FB_Step_With_Enc.DB_Motor_4_WithEnc(

Motor_Controler_Addr := 296 // IN: INT

,DO_Addr := 3 // IN: INT

,DI_Addr := 3 // IN: INT

,ColdStart := TRUE // IN: BOOL

,Encoder_Type := 1 // IN: BOOL

,G_multiplier := 20 // IN: INT

);

(*****                                                                 *****)

(*****             Clod Start Organisation Block END                   *****)

(***************************************************************************)

END_ORGANIZATION_BLOCK

ORGANIZATION_BLOCK OB_Main

(***************************************************************************)

(*****                  Main Organisation Block                        *****)

(*****                                                                 *****)

VAR_TEMP

// Reserved

Info: ARRAY[0..19] OF BYTE;

// Temporary Variables

END_VAR

// Motor 1 Part

FB_Step_Without_Enc.DB_Motor_1_WithoutEnc(

Motor_Controler_Addr := 272 // IN: INT

,DO_Addr := 0 // IN: INT

,DI_Addr := 0 // IN: INT

,ColdStart := FALSE // IN: BOOL

,AutoReg := DB_FF37_dctfimag_01.CMD.Order // IN: WORD

,Auto_Set_Position := DB_FF37_dctfimag_01.CMD.requestedPosition // IN: REAL

,Auto_Mode_Command := DB_FF37_dctfimag_01.CMD.commandMode // IN: WORD

,Ref_Position := DB_FF37_dctfimag_01.CFG.refPosition

,In_Min_limit := DB_FF37_dctfimag_01.CFG.minPosition

,In_Max_limit := DB_FF37_dctfimag_01.CFG.maxPosition

,In_Scal := DB_FF37_dctfimag_01.CFG.scalingFactor

,In_Offset := DB_FF37_dctfimag_01.CFG.offset

,IePlcConfig := DB_FF37_dctfimag_01.CFG.config

);

DB_FF37_dctfimag_01.AQN.status1 := DB_Motor_1_WithoutEnc.Status1; // OUT: WORD

DB_FF37_dctfimag_01.AQN.status2 := DB_Motor_1_WithoutEnc.Status2; // OUT: WORD

DB_FF37_dctfimag_01.AQN.targetPosition := DB_Motor_1_WithoutEnc.Obj_Set_Position; // OUT: REAL

DB_FF37_dctfimag_01.AQN.actualPosition := DB_Motor_1_WithoutEnc.Obj_Actual_Position; // OUT: REAL

//Motor 4 Part

FB_Step_With_Enc.DB_Motor_4_WithEnc(

Motor_Controler_Addr :=  296// IN: INT

,DO_Addr := 3 // IN: INT

,DI_Addr := 3 // IN: INT

,ColdStart := FALSE // IN: BOOL

,Encoder_Type := 1 // IN: BYTE

,Factor_Encoder := 5 // IN: INT

,AutoReg := DB_FF37_dctfimag_04.CMD.order // IN: WORD

,Auto_Set_Position := DB_FF37_dctfimag_04.CMD.requestedPosition // IN: REAL

,Auto_Mode_Command := DB_FF37_dctfimag_04.CMD.commandMode // IN: WORD

,In_Min_limit := DB_FF37_dctfimag_04.CFG.minPosition

,In_Max_limit := DB_FF37_dctfimag_04.CFG.maxPosition

,In_Scal := DB_FF37_dctfimag_04.CFG.scalingFactor

,In_Offset := DB_FF37_dctfimag_04.CFG.offset

,IePlcConfig := DB_FF37_dctfimag_04.CFG.config

);

DB_FF37_dctfimag_04.AQN.status1 := DB_Motor_4_WithEnc.Status1; // OUT: WORD

DB_FF37_dctfimag_04.AQN.status2 := DB_Motor_4_WithEnc.Status2; // OUT: WORD

DB_FF37_dctfimag_04.AQN.targetPosition := DB_Motor_4_WithEnc.Obj_Set_Position; // OUT: REAL

DB_FF37_dctfimag_04.AQN.actualPosition := DB_Motor_4_WithEnc.Obj_Actual_Position; // OUT: REAL

FC_dctfimag(); // Call function for IEPLC communication.

(*****                                                                 *****)

(*****                  Main Organisation Block END                    *****)

(***************************************************************************)

END_ORGANIZATION_BLOCK

DB_FF37_dctfimag_01 and DB_FF37_dctfimag_04 are the DBs generated by the IEPLC generator.

### ANNEXE 2: Local Panel Example

A template application is available for local control. Here, a TP177A touch panel is used.

Content of the panel:

Upper left box: contains the status of the limit switches and the software limits.

Lower left box: contains the scale and the offset which determine the ratio between physical and absolute positions.

Upper right box: contains the status of actual physical and absolute positions, the last “Local Set Position” (the value can be change with this button), the “Object Set Position”  which can be different from “Local Set Position” when the object is in “Auto” or “Manu”.

Lower middle box: contains actual mode of control.

Lower right box: contains the selected type of movement and “Synchronized” indicate that the “Search Reference” has been executed.

Lower buttons: The left button select the “Auto Mode” when the object is in “Local Mode”, the 3 others select the type of movement.